## Slide 1: Revealing Structural and Functional Vulnerability of Power Grids to Cascading Failures
      Junyuan Fang1,2, Jiajing Wu2, Zibin Zheng2, Chi K. Tse1
      1 City University of Hong Kong
      2 Sun Yat-sen University

## Slide 2
      Introduction
      Models
      Optimal attack based on multi-objective optimization
      Vulnerability and critical nodes analysis
      Conclusion and future work

## Slide 3
      Introduction
      Models
      Optimal attack based on multi-objective optimization
      Vulnerability and critical nodes analysis
      Conclusion and future work

## Slide 4: Introduction
      Power grid
      Widely exist in our daily life
          Typical complex network
          Critical infrastructure of modern society
        Cascading failure propagation
          Complex connection between nodes
          Increasingly network scale
        Large-scale blackouts
          2006 in Germany
          2008 in India
          2016 in Ukraine
        Vulnerability concern

## Slide 5: Introduction
      Vulnerability of power grids
      Vulnerability against malicious attacks
      Vulnerable network  small tolerance to malicious attacks  poor performance
      Cascading failures
      The failure of a single node may cause the failure of its neighbors
      Power grids: the malfunctioning of a few components may trigger successive breakdowns across the whole system

## Slide 6: Introduction
      Why investigates the vulnerability of power grids?
      Power grids play an important role in our daily life
          Cascading failure may lead to large-scale blackouts
          The failure of critical nodes will cause a heavy damage to the system
        Urgent problem
          How to estimate the vulnerability of power grids in complex environments?
      Goal
      Vulnerability analysis
          From different investigation perspectives
      Critical nodes identification
          Identify critical nodes to help for further protection

## Slide 7
      Introduction
      Models
      Optimal attack based on multi-objective optimization
      Vulnerability and critical nodes analysis
      Conclusion and future work

## Slide 8: Models
      Basic component
      Generator nodes
      Demand nodes
      Transmission links
      Boundaries of generator nodes
      Increase
      Decrease
      Power flow calculation
      DC power flow model

## Slide 9: Models
      Cascading failure model
      Initialization
          Initialize the power and topology parameters
      Launch of attack
          Remove the selected nodes
      Subgraph detection
          Remove the subgraphs which only have a single node or do not have the generator nodes
      Power re-dispatch and flow re-calculation
          Adjust the power output of generator nodes to achieve system balance
      Link overload detection
          Trip the link with the heaviest overloading

## Slide 10
      Introduction
      Models
      Optimal attack based on multi-objective optimization
      Vulnerability and critical nodes analysis
      Conclusion and future work

## Slide 11: Optimal attack based on multi-objective optimization
      Vulnerability from different perspectives
      Topological: measures the structural properties of the system
      Functional: measures the intended function of a specific system
      Both topological and functional perspectives are critical
      Current works: focus on single perspective
      Problem transformation
      From the perspective of attackers, we investigate the vulnerability of power grids by attacking the power nodes in the system
      Critical nodes identification: node selection problem
      Analyze the relationship between different vulnerability perspectives, and the influence of different node attack strategies

## Slide 12: Optimal attack based on multi-objective optimization
      Structural vulnerability (SV)
      The change of the largest connected subgraph size before and after the cascading failure process
      Functional vulnerability (FV)
      The change of the total power demand before and after the cascading failure process

## Slide 13: Optimal attack based on multi-objective optimization
      Relationship between SV and FV
      Dataset
          IEEE 118/300
      Random attack
          Setting: randomly remove 25 and 30 nodes, respectively
        Results
          Higher SV/FV do not indicates higher FV/SV
          A specific value of SV/FV will have a series of different value of FV/SV
IEEE118
IEEE300

## Slide 14: Optimal attack based on multi-objective optimization
      Relationship between SV and FV
      Intentional attack
          Setting: utilize genetic algorithm to attack SV and FV, respectively
        Results
          Maximizing SV/FV could not always maximizing FV/SV
IEEE118, SV
IEEE118, FV

## Slide 15: Optimal attack based on multi-objective optimization
      Relationship between SV and FV
      Intentional attack
          Setting: utilize single genetic algorithm to attack SV and FV, respectively
        Results
          Maximizing SV/FV could not always maximizing FV/SV
          These two metrics are conflicts with each other
IEEE300, SV
IEEE300, FV

## Slide 16: Optimal attack based on multi-objective optimization
      Multi-objective optimization problem
      Final goal includes multiple different sub-problems
      These sub-problems are conflicts with each other
      Multi-objective optimization based on Pareto front
          Optimized by the dominating relation between solutions
          Pareto front: A series of non-dominated solutions
          Example: A and B
        Analyze the vulnerability of power grids from SV and FV at the same time

## Slide 17: Optimal attack based on multi-objective optimization
      Multi-objective power grids attack method: NSGA-PG
      Based on effective NSGA-II, we proposes NSGA-PG which is suitable for our scenario
      Main steps
        Individual crossover and mutation
          Obtain better individuals by exchanging the individual information and external mutation
          Improve the searching ability
          Conflict solving strategy

## Slide 18: Optimal attack based on multi-objective optimization
      Main steps
        Individual discard (new)
          Remove the duplicate individuals in each iteration, and randomly generate new individuals
          Reduce the waste of computing resources on the same individuals
        Vulnerability calculation and non-dominated sorting
          Assume the nodes in the individuals as an attack node-list
          Remove the corresponding nodes in the system, and calculate SV and FV after cascading failure process
          Record the superiority of each individual based on non-dominated sorting

## Slide 19: Optimal attack based on multi-objective optimization
      Main steps
        Elite selection
          Reserve the individuals with higher dominated rankings
        Termination
          The individuals in the optimal subset (e.g., ) do not change in 30 iterations
          Exceed the predefined maximum number of iterations

## Slide 20
      Introduction
      Models
      Optimal attack based on multi-objective optimization
      Vulnerability and critical nodes analysis
      Conclusion and future work

## Slide 21: Vulnerability and critical nodes analysis
      Optimal solution analysis
        Generally, the node with a higher degree and power load will have a higher influence on the power system
        Case study 1: how do the degree and load influence SV/FV?
          Analysis: the node’s ranking on degree and load properties
          Setting: IEEE300, maximize SV/FV
          Results
            SV prefers to select the nodes with higher degree
            FV prefers to select the nodes with higher load
IEEE300, SV
IEEE300, FV

## Slide 22: Vulnerability and critical nodes analysis
      Optimal solution analysis
        Critical nodes reservation: only reserve the nodes with higher degree or load through parameter
        Case study 2: the degree and load of the nodes in the Pareto front obtained by NSGA-PG?
          Node coverage function
          Given a particular value of , a higher value of means NSGA-PG is more likely to select the nodes have higher degree or power load

## Slide 23: Vulnerability and critical nodes analysis
      Optimal solution analysis
        Case study 2: the degree and load of the nodes in the Pareto front obtained by NSGA-PG?
          Setting: the value of is begin from 5 to 50, step = 5
          Results
            If increase, will also increase
            A relatively small (30) can achieve a high (80%)
            When =50,
            Most of the nodes in the Pareto front are the nodes with the top 30% degree or power load

## Slide 24: Vulnerability and critical nodes analysis
      The influence of 𝛼
        Reduce the size of candidate nodes can significantly reduce the searching space
        Propose optimized algorithm: NSGA-PGCN,
      NSGA-PGCN
        Compare to NSGA-PG, the new proposed NSGA-PGCN only retain the nodes with the top 30% degree or power load
        Significantly reduce the searching space, which can improve the possibility of obtaining a better Pareto front

## Slide 25: Vulnerability and critical nodes analysis
      Experiment 1: compare with heuristic methods
        Baselines: High degree (HD), High load (HL), High betweenness (HB), High closeness (HC), Random (RA)
        The solution of NSGA-PG and NSGA-PGCN: select the solution from the Pareto front with the largest Euclidean distance to the origin
        Results
          Baselines only focus on single metric
          NSGA-PG and NSGA-PGCN obtain a better trade-off performance
          NSGA-PGCN is better than initial NSGA-PG
IEEE300

## Slide 26: Vulnerability and critical nodes analysis
      Experiment 2: compare with single-objective methods
        Compare with three different objective functions
        Baselines
          Genetic algorithm based strategy (GA)
          Load distribution vector based strategy (LDV)
          Reduced search space based strategy (RSS)
          Risk graph based strategy (RG)

## Slide 27: Vulnerability and critical nodes analysis
      Experiment 2: compare with single-objective methods
        Results
          Single-objective methods can only obtain a single solution, while multi-objective methods can obtain a series of non-dominated solutions
          The above three different objectives (, , and ) are close to the left, middle, and right part of the Pareto fronts
          The proposed two multi-objective methods can obtain a comparable or even better solution than the single-objective methods
IEEE118
IEEE300

## Slide 28: Vulnerability and critical nodes analysis
      Experiment 3: comparisons between NSGA-PG and NSGA-PGCN
        Evaluate metrics: solution diversity (D), iteration times for convergence (I), hyper volume (HV)
        Setting: 50 times repetition on two methods, respectively
        Results
          NSGA-PG has a relatively larger D
          NSGA-PGCN has faster convergence speed I in four datasets

## Slide 29: Vulnerability and critical nodes analysis
      Experiment 3: comparisons between NSGA-PG and NSGA-PGCN
        Evaluate metrics: solution diversity (D), iteration times for convergence (I), hyper volume (HV)
        Setting: 50 times repetition on two methods, respectively
        Results
          NSGA-PGCN can obtain an averagely better HV in four datasets
          Based on Wilcoxon rank sum test, we can conclude that, NSGA-PGCN significantly outperforms NSGA-PG in terms of HV at the level of 5%

## Slide 30: Vulnerability and critical nodes analysis
      Experiment 4: sensitivity analysis on parameter 𝛼
        Setting: the value of 𝛼 is begin from 5 to 50, step = 5
        Results
          HV slowly increases with up to around
          When , HV begins to decrease in all datasets
        The detailed experimental results can be found in our paper
IEEE118
IEEE300

## Slide 31
      Introduction
      Models
      Optimal attack based on multi-objective optimization
      Vulnerability and critical nodes analysis
      Conclusion and future work

## Slide 32: Conclusion and future work
      Conclusion
        Employ a more accurate cascading failure model based on DC power flow calculation
          Separate the cascading failure process, link overload detection
        Revealing the vulnerability of power grids from structural and functional perspectives
          Consider SV and FV at the same time, metric confliction analysis
        Propose two multi-objective node attack strategies based on NSGA-II
          NSGA-PG, node selection preference (SV and degree, FV and power load), NSGA-PGCN
      Future work
        Sequential node attack strategy
        False data injection attacks
        Defense against intentional attacks

## Slide 33
      Thanks for your attention!
      Q&A
      Paper: https://ieeexplore.ieee.org/abstract/document/9235529
      Code: https://github.com/alexfanjn/multi-objective-attack-power-grid
      Contact: Junyuan Fang(email: junyufang2-c@my.cityu.edu.hk)